## Tables 1, 2, 3
Worksheet Cover Sheet
EVALUATION WORK SHEETS FOR
THE FIRE AND LIFE SAFETY INDEX FOR
EXISTING RESIDENTIAL HIGH-RISE BUILDINGS
FACILITY: |  |  |  |  | BUILDING:
FIRE COMPARTMENTS(S) EVALUATED
EVALUATOR: |  |  |  |  | DATE:
PURPOSE:
X
Complete this work sheet for each fire compartment (floor) Where conditions are the same in several fire compartments, one work sheet sheet can be used for those fire compartments.
X
HAVE A MAJORITY OF THE UNIT OWNERS VOTED TO OPT OUT OF REQUIRED SPRINKLER PROTECTION? | [6 empty] | << Answer by placing a "Yes" or "No" in the box on the left.
THE SPRINKLER OPT-OUT VERSION OF THE LIFE SAFETY EVALUATION DOES NOT PROVIDE AN EQUIVALENT LEVEL OF LIFE SAFETY TO BUILDING OCCUPANTS AND FIRE FIGHTERS.
Existing highrise residential building means any building that has floors used for human occupancy located more than 75 feet above the highest grade and contains dwelling units.
Table 1. Occupant and Firefighter Risk Parameters
Risk Parameters |  |  |  | RISK PARAMETER VALUES | [7 empty] | #DIV/0!
|  |  | MOBILITY |  | NORMAL OR LIMITED | REQUIRE* | *If the building fire emergency plan contains provisions which identify those building occupants that require assistance and establish procedures for the safe evacuation of these occupants, the risk values for "Normal or Limited Mobility" can be used.
1.RESIDENT EVACUATION CAPABILITY |  |  | STATUS |  | MOBILITY | ASSISTANCE
|  |  | OCCUPANT RISK FACTOR (O1) |  | 1.5 | 2.5 | [5 empty] | #DIV/0!
|  |  | FIREFIGHTER RISK FACTOR (FF1) |  | 1.6 | 3
ENTER (O1)
ENTER (FF1)
2. OCCUPANT LOAD |  |  | RESIDENTS | 1 TO 25 | 26 TO 50 | 51 TO 100 | > 100
|  |  | OCCUPANT RISK FACTOR (O2) | 1 | 1.1 | 1.2 | 1.3
|  |  | FIREFIGHTER RISK FACTOR (FF2) | 1 | 1.1 | 1.2 | 1.3
ENTER (O2) |  |  | The occupant load is |  |  | persons
ENTER (FF2)
3. FIRE COMPARTMENT LOCATION (L) |  |  | FLOOR | 9TH FLOOR OR LOWER | 10TH TO 19TH | 20TH TO 29TH | > 30TH
|  |  | OCCUPANT RISK FACTOR (O3) | 1.1 | 1.2 | 1.3 | 1.4
|  |  | FIREFIGHTER RISK FACTOR (FF3) | 1.1 | 1.5 | 1.8 | 2
ENTER (O3) |  |  | Highest floor with residential dwellings is |  |  |  |  | floor.
ENTER (FF3)
Table 2. Risk Factor Calculations
|  | O1 |  | O2 |  | O3 |  | ORF
OCCUPANT RISK FACTOR (ORF) |  | 0 | X | 0 | X | 0 | = | 0
|  | FF1 |  | FF2 |  | FF3 |  | FFRF
FIREFIGHTER RISK FACTOR (FFRF) |  | 0 | X | 0 | X | 0 | = | 0
Table 3A and 3B Building Status
| Table 3A. New Buildings | [5 empty] | Table 3B. (Existing Buildings)
|  |  | ORF |  | ORF |  |  |  | ORF |  | ORF
| 1 | x | 0 | = | 0 |  | 0.6 | x | 0 | = | 0
|  |  | FFRF |  | ORF |  |  |  | FFRF |  | FFRF
| 1 | x | 0 | = | 0 |  | 0.6 | x | 0 | = | 0
This facility is an existing building.
OCCUPANT RISK FACTOR (ORF) |  | 0
FIREFIGHTER RISK FACTOR (FFRF) |  | 0

## Table 4
Table 4 Fire Safety Parameter Values
| Parameters | Parameter Values
NONCOMBUSTIBLE
1 | CONSTRUCTION TYPE |  | TYPES I AND II
|  | TYPE IIB, TYPE III, V | TYPE IIA (ONE HOUR) | TYPE IA or 1B (FIRE RESISTIVE)
LOCATION OF FIRE COMPARTMENT (Floor above level of exit discharge)
| 9TH OR LESS | NP | NP | 2
| 10TH TO 15TH | NP | NP | 1
| 16TH TO 20TH | NP | NP | 0
| 21ST TO 30TH | NP | NP | -1
| 30TH AND ABOVE | NP | NP | -2
ENTER 1.
2 | INTERIOR FINISH (Corridors and Exits) | UNDETERMINED OR LESS THAN CLASS C | CLASS C | CLASS B | CLASS A*
|  | -10 | -5 | -2 | 3 |  | * Interior finish of Class B or less that is provided with a listed, approved fire retardant coating, providing a Class A rating, is acceptable.
ENTER 2.
3 | CORRIDOR & DWELLING UNIT SEPARATION WALLS | NONE OR INCOMPLETE | < 1/2 HR. | >1/2< 1 HR | > 1 HR
|  |  |  | NON-MASONRY (e.g. gypsum wall board stud partition) | MASONRY OR CONCRETE * | * For locations where there are no interior corridors, only exterior egress balconies, use 4 points, regardless of wall type.
|  | -10 | -5 | 0 | 4
ENTER 3.
4 | DOORS TO CORRIDOR * | NO DOOR OR DOOR CONTAINS UNPROTECTED OPENINGS | <20 MIN. FPR NO CLOSER | <MIN 1 3/4 INCH SOLID WOOD CORE WITH CLOSER | MININUMUM 20 MIN. FPR WITH CLOSER
|  | -10 | -5 | 2 | 5 | * For buildings with exterior egress balconies enter 5 regardless of door type
ENTER 4.
5 | EXIT ACCESS*
|  | MAXIMUM CORRIDOR DEAD END |  |  | NO DEAD END > 20
5A. | INTERIOR CORRIDOR | >100 FEET | 51' - 100' | 21' - 50' | TRAVEL DISTANCE >150 FEET | 100' - 150' | <100 FEET | * Use (0) where Parameter 9 is – 8.
|  | -8 | -6 | -4 | 0 | 1 | 2
|  | MAXIMUM CORRIDOR DEAD END |  |  | NO DEAD END > 30
5B. | EXTERIOR EGRESS BALCONIES (EXTERIOR EXIT ACCESS) | >100' | 50' - 100' | 30' - 50' | TRAVEL DISTANCE >150' | 100' - 150' | <100 FEET
|  | -4 | -2 | -1 | 1 | 4 | 8
ENTER 5.
|  | OPEN 4 OR MORE |  | OPEN 2 OR 3 | ENCLOSED WITH INDICATED FIRE RESISTANCE |  | * The licensed design professional should determine the representative sampling amount in order to provide the value for this parameter
6 | VERTICAL OPENINGS | FLOORS |  | FLOORS | < 1 HR | >=1 HR<2 HR
|  | -14 |  | -10 | 0 | 2
ENTER 6.
|  | DOUBLE DEFICIENCY |  | SINGLE DEFICIENCY |  | NO DEFICIENCIES
7 | HAZARDOUS AREAS | IN FIRE COMPARTMENT | OUTSIDE FIRE COMPARTMENT | IN FIRE COMPARTMENT | OUTSIDE FIRE COMPARTMENT
|  | -11 | -5 | -6 | -2 | 0
ENTER 7.
|  | NONE | SMOKEPROOF ENCLOSURE | EXTERIOR STAIRS OR STAIR SHAFT WITH EXTERIOR EXIT ACCESS FOR ALL EXIT STAIRS | SMOKEPROOF ENCLOSURE (VIA NATURAL VENTILATION OR MECHANICAL PRESSURIZATION) | MECHANICAL SMOKE CONTROL WITHIN FIRE COMPARTMENT OR FLOOR IS SUBDIVIDED INTO ONE OR MORE SMOKE COMPARTMENTS
8 | SMOKE MANAGEMENT |  | IN ONLY ONE EXIT STAIR |  | ALL EXIT STAIRS
|  | -5 | -2 | 3 | 4 | 4
ENTER 8.
9 | EGRESS ROUTES | < 2 ROUTES | MULTIPLE ROUTES
|  |  | DEFICIENT | NOT DEFICIENT | NOT DEFICIENT W/ COMPLIANT STAIRWELL REENTRY
|  | -8 | -2 | 0 | 3
ENTER 9.
10 | FIRE ALARM SYSTEM | NONE, NONOPERATIONAL, OR NONCOMPLIANT | MANUAL INITIATION WITHOUT FIRE DEPARTMENT NOTIFICATION
|  |  | OCCUPANT NOTIFICATION WITHOUT VOICE COMMUNICATION | OCCUPANT NOTIFICATION WITH VOICE COMMUNICATION
|  | -10 | 1 | 4
ENTER 10.
|  | NONE | CORRIDORS * |  |  | TOTAL SMOKE DETECTION THROUGHOUT FIRE COMPARTMENT | * For locations where there are no interior corridors, only exiterior egress balconies, use 3 points, even if there is no smoke detection.
11 | SMOKE DETECTION
|  | 0 (3) ** | 3 |  |  | 5 | ** Use this value if the entire zone is protected with quick-response automatic sprinklers.
ENTER 11.
|  | NONE | CORRIDOR & COMMON AREAS | ENTIRE BUILDING WITH NFPA 13R ON RESIDENTIAL FLOORS | ENTIRE BUILDING * | * For locations where there are no interior corridors, only exterior egress balconies, use 5 points, even if there is no sprinkler protection
12 | AUTOMATIC SPRINKLERS
|  | -8 (0)** (-6)*** | 0 | 8 | 10 (5)* | ** For locations which have opted out of sprinkler protection, use 0 points.
| ENTER 23. |  |  |  |  | *** Item 1 is 2 points use -6 points here
13 | SMOKE ALARMS | NONE | ONE IN HALL NEAR BEDROOM | ONLY IN BEDROOM(S) | IN ALL BEDROOMS AND HALLWAYS NEAR BEDROOMS NO TANDEM OPERATION | IN ALL BEDROOMS AND HALLWAYS NEAR BEDROOMS WITH TANDEM OPERATION
|  | -10 | -2 | -1 | 2 | 4
ENTER 13.
|  | NONE | CLASS I STANDPIPE PRESENT BUT NOT IN ALL REQUIRED EXITS | CLASS 1 MANUAL STANDPIPE IN ALL EXIT ENCLOSURES | AUTOMATIC WET STANDPIPE SYSTEM WITH HOSE VALVES IN ALL EXIT ENCOSURES | * COMBINED SYSTEM WITH HOSE VALVES IN ALL EXIT ENCOSURES | * Credit for a combined system is only permitted if the Parameter 13 Automatic Sprinklers value is 8 or 10
14 | STANDPIPE SYSTEM
|  | -10 | 0 | 5 | 7 | 10
ENTER 14.
15 | ELEVATORS | NO RECALL OR NO FIREFIGHTER SERVICE | WITH RECALL AND FIREFIGHER SERVICE
|  |  | NO EMERGENCY POWER | EMERGENCY POWER
|  | -5 | 0 | 4
ENTER 15.
16 | EMERGENCY LIGHTING AND EXIT SIGNS | NO EMERGENCY LIGHTING | EXITS ONLY | EXIT ACCESS AND EXITS
|  | -2 | 0 | 2
ENTER 16.
NP | Not permitted, this evaluation method cannot be used.

## Table 5
Table 5 Individual Safety Evaluations
| FIRE SAFETY PARAMETER | COMPARTMENTATION FIRE SAFETY (S1) | EXTINGUISHMENT FIRE SAFETY (S2) | EGRESS FIRE SAFETY (S3) | GENERAL OCCUPANT SAFETY (S4) | GENERAL FIRE FIGHTER SAFETY (S5)
1 | CONSTRUCTION | 0 | 0 |  | 0 | 0
2 | INTERIOR FINISH (Corridors and Exits) | 0 |  | 0 | 0 | 0
3 | CORRIDOR & DWELLING UNIT SEPARATION WALLS | 0 |  |  | 0 | 0
4 | DOORS TO CORRIDOR *
|  | 0 |  | 0 | 0 | 0
5 | EXIT ACCESS*
|  |  |  | 0 | 0 | 0
6 | VERTICAL OPENINGS
|  | 0 |  | 0 | 0 | 0
7 | HAZARDOUS AREAS | 0 | 0 |  | 0 | 0
8 | SMOKE MANAGEMENT
|  |  |  | 0 | 0 | 0
9 | EGRESS ROUTES |  |  | 0 | 0 | 0
10 | FIRE ALARM SYSTEM |  |  |  |  | use 1/2 of item 10
|  |  | 0 |  | 0 | 0
11 | SMOKE DETECTION |  | 0 | 0 | 0 | 0
12 | AUTOMATIC SPRINKLERS |  | 0 | 0 | 0 | 0
13 | SMOKE ALARMS |  |  | 0 | 0
14 | STANDPIPE SYSTEM |  | 0 |  |  | 0
15 | ELEVATORS |  |  |  |  | 0
16 | EMERGENCY LIGHTING AND EXIT SIGNS |  |  | 0 | 0 | 0
| SUBTOTALS | 0 | 0 | 0 | 0 | 0
| ADDITIONAL FACTORS |  |  | OCCUPANT RISK FACTOR | OCCUPANT RISK FACTOR | FIREFIGHTER RISK FACTOR
|  |  |  | 0 | 0 | 0
|  | S1 = | S2 = | S3 = | S4 = | S5 =
| TOTAL VALUE | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0!

## Table 6
Table 6 Minimum Required Fire Safety Indices
| COMPARTMENT FIRE SAFETY Sa |  | EXTINGUISHMENT FIRE SAFETY Sb |  | EGRESS FIRE SAFETY Sc |  | GENERAL OCCUPANT FIRE SAFETY Sc |  | FIRE FIGHTER SAFETY
| Sa |  | Sb |  | Sc |  | Sd |  | Se
|  | EXIST. |  | EXIST. |  | EXIST. |  | EXIST. |  | EXIST.
STANDARD INDICES |  | 8 |  | 8 |  | 8 |  | 8 |  | 8
OPT-OUT INDICES |  | 6 |  | 6 |  | 8 |  | 6 |  | 6
HAVE A MAJORITY OF THE UNIT OWNERS VOTED TO OPT OUT OF REQUIRED SPRINKLER PROTECTION | [9 empty] | 0 | This answer is from cell G17 in Table 1
IF THE ANSWER IS YES,THEN PROCEED WITH THE OPT OUT VERSION
THE SPRINKLER OPT-OUT VERSION OF THE LIFE SAFETY EVALUATION DOES NOT PROVIDE AN EQUIVALENT LEVEL OF LIFE SAFETY TO BUILDING OCCUPANTS AND FIRE FIGHTERS.
| Sa = | 8 | Sb = | 8 | Sc = | 8 | Sd = | 8 | Se = | 8

## Table 7
Table 7. Fire Compartment Safety Equivalency Evaluation | [7 empty] | YES | NO
CALCULATED FIRE SAFETY INDEX |  | MINIMUM REQUIRED FIRE SAFETY INDEX | [5 empty] | Is C >=0?
|  |  | S1 |  | Sa |  | C
COMPARTMENTATION FIRE SAFETY (S1) | less | COMPARTMENT FIRE SAFETY (Sa) | 0 | - | 8 | = | -8 |  | X
|  |  | S2 |  | Sb |  | E | Is E >=0?
EXTINGUISHMENT FIRE SAFETY (S2) | less | EXTINGUISHMENT FIRE SAFETY (Sb) | 0 | - | 8 | = | -8 |  | X
|  |  | S3 |  | Sc |  | P | Is P >=0?
EGRESS FIRE SAFETY (S3) | less | EGRESS FIRE SAFETY (Sc) | #DIV/0! | - | 8 | = | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | S4 |  | Sd |  | G | Is G >=0?
GENERAL OCCUPANT SAFETY (S4) | less | GENERAL OCCUPANT SAFETY (Sd) | #DIV/0! | - | 8 | = | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | S5 |  | Se |  | F | Is F >=0?
FIRE FIGHTER SAFETY (S5) | less | FIRE FIGHTER SAFETY (SE) | #DIV/0! | - | 8 | = | #DIV/0! | #DIV/0! | #DIV/0!

## xx (hidden)
Table 8 Facility Firesafety Requirements Work Sheet
|  | MET | NOT | NOT
|  |  | MET | APP
A. | Building Utilities conform to the requirements of applicable codes and standards | X
C. | HVAC systems conform with the air conditioning, heating, and ventilating systems requirements of applcable codes and standards, except for enclosure of vertical openings, which have been considered in Safety Parameter 7 of Table 4 | X
D. | Fuel burning space heaters and portable electrical space heaters are not used. | X
E. | There are no flue fed incinerators. | X
F. | An evacuation plan is provided and fire drills conducted in accordance with Subsections 31.1.5, 31-4.1, and | X
31-4.2
G. | Smoking regulations have been adopted and implemented in accordance with Subsection 31-4.4 | X
H. | Draperies, upholstered furniture, mattresses, furnishings, and decorations combustibility is | X
limited in accordance with 12-7.5 and 13-7.5.
I. | Fire extinguishers are provided in accordance with the requirements of 12-3.5.4 & 13-3.5.7. | X
J. | Exit signs are provided in accordance with the requirements of 12-2.10.1 & 13-2.10. | X
K. | Emergency lighting is provided in accordance with 12-2.9.1 or 13-2.9 | X
L | Standpipes are provided in all new high rise buildings as required by 12-4.2 |  |  | X

## Table 8
TABLE 8 CONCLUSIONS
All of the checks in Table 7 are in the "Yes" column. The level of fire safety is acceptable.
One or more of the checks in Table 7 are in the "No" column. The level of fire safety is not acceptable.
Compliance will be met with an automatic fire sprinkler system throughout the building.